## Worksheet
FY20 | Electric Unitary HVAC -03
Customer Information | [15 empty] | Total Units Committed: |  |  | 0
Name | [7 empty] | Address | [7 empty] | Total Units Installed: |  |  | 0
Date
Contact | [30 empty] | Pre-Inspection Notes |  |  | Post-Inspection Notes
Contractor/Vendor Information | [25 empty] | Inspection Type
Name | [7 empty] | Address
Contact | [7 empty] | Phone
Enhanced Incentive Eligibility
FALSE | FALSE | FALSE
FALSE | FALSE | FALSE | [36 empty] | Date | Inspector/Sign-off
| Incentive amounts below are estimated based on standard program incentives. These values and any additional enhancements will be verified by the Program Manager prior to approval. | [36 empty] | Pre-Inspection
Project Type | [7 empty] | Building Type | [7 empty] | Totals: |  | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post Inspection
Measure Code | Reason | Type | Manufacturer | Model | Occ. Cont. T-Stat Only |  |  |  | Unit Size Cooling | Unit Cooling Efficiency | AC & ASHP ≥ 65,000 Btuh Only | HP And Occ. Cont.T-Stat Only |  | Quantity Committed | Quantity Installed | Incentive Per Unit | Enhanced Incentive Per Unit | Total Committed Incentive | Total Installed Incentive | Baseline Efficiency Cooling | Baseline Efficiency Cooling | Baseline Efficiency Heating | Peak Demand Savings per Unit | Annual Cooling Savings per Unit | Annual Heating Savings per Unit | Total Annual Savings per Unit | Annual Heating Savings per Unit | Peak Demand Savings Committed | Peak Demand Savings Installed | Annual Energy Savings Committed | Annual Energy Savings Installed | Annual Energy Savings Committed | Annual Energy Savings Installed | Lifetime Energy Savings Committed | Lifetime Energy Savings Installed | Lifetime Energy Savings Committed | Lifetime Energy Savings Installed
| N-New | <Hover over cell C12 for abbreviation definitions> |  |  | Heating Season Facility Temp. | Heating Type | Cooling Season Facility Temp. | Weekly Occupied Hours |  |  |  | Unit Size Heating | Heating Efficiency | [24 empty] | FOUND PRE |  | FOUND POST
| R-Replaced |  |  |  |  | E - Electric |  |  | (Btuh) | (SEER or EER) <Hover over cell K12 for units> | Unit Cooling Efficiency |  | (HSPF, COP, AFUE, Et, or Ec) <Hover over cell N13 for units> | [10 empty] | (kWh) | (kWh) | (kWh) | (Therms) | [10 empty] | (Type) | Count | (Type) | Count
[6 empty] | G - Gas | [5 empty] | (Btuh) | [7 empty] | (SEER or EER) | (IEER) | (HSPF or COP | [5 empty] | (kW) | (kW) | (kWh) | (kWh) | (Therms) | (Therms) | (kWh) | (kWh) | (Therms) | (Therms)
[8 empty] | (use 84 as default) |  |  | (IEER) | [11 empty] | (kW)
[5 empty] | (°F) |  | (°F)
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Project in UEZ
Project in OZ
Municipality
K-12 School
County
Affordable Housing
Note on C14: Measure Abbreviations S - Split System (<20 Tons) P - Single Package (<20 Tons) D - Central DX AC (≥20 Tons) AS - Split System ASHP AP - Single Package ASHP W - WSHP PTAC - Packaged Terminal AC PTHP - Packaged Terminal HP PVAC - Packaged Vertical AC PVHP - Packaged Vertical HP O - Occupancy Controlled Thermostat E - A/C Economizing Control
Note on K14: Cooling Efficiency Units Split System, Single Package, Central DX AC, Split System ASHP, Single Package ASHP with <65,000 Btuh cooling capacity: SEER All others: EER For A/C Economizing Control, a default 9.5 EER may be used.
Note on N15: Heating Efficiency Units Split System ASHP, Single Package ASHP with <65,000 Btuh cooling capacity: HSPF All other electric heating systems: COP Gas heating systems: AFUE, Et or Ec

## Measure Codes (hidden)
Measure Code | Type Abbreviation | System Type | Min Capacity (BTUh | Max Capacity (BTUh | Baseline SEER | Baseline HSPF | Baseline EER | Baseline IEER | Baseline COP | Min Qualifying SEER EB | Min Qualifying SEER NC | Min Qualifying HSPF EB | Min Qualifying HSPF NC | Min Qualifying EER EB | Min Qualifying EER NC | Min Qualifying IEER EB | Min Qualifying IEER NC | Min Qualifying COP EB | Min Qualifying COP NC | Incentive per Ton EB | Incentive per Ton NC | Measure Life | Tier
HVAC1 | S | Split System - S | 1 | 64999 | 13 | N/A | N/A | N/A | N/A | 14 | 14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 92 | 92 | 15 | 1
HVAC2 | S | Split System - S | 1 | 64999 | 13 | N/A | N/A | N/A | N/A | 16 | 16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 105 | 105 | 15 | 2
HVAC3 | P | Single Package - P | 1 | 64999 | 14 | N/A | N/A | N/A | N/A | 14.3 | 14.3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 92 | 92 | 15 | 1
HVAC4 | P | Single Package - P | 1 | 64999 | 14 | N/A | N/A | N/A | N/A | 16 | 16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 103 | 103 | 15 | 2
HVAC5 | S | Split System - S | 65000 | 134999 | N/A | N/A | 11 | 12.7 | N/A | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 13 | 13 | N/A | N/A | 73 | 73 | 15 | 1
HVAC6 | S | Split System - S | 65000 | 134999 | N/A | N/A | 11 | 12.7 | N/A | N/A | N/A | N/A | N/A | 12.5 | 12.5 | 14 | 14 | N/A | N/A | 79 | 79 | 15 | 2
HVAC7 | S | Split System - S | 135000 | 239999 | N/A | N/A | 10.8 | 12.2 | N/A | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 12.4 | 12.4 | N/A | N/A | 79 | 79 | 15 | 1
HVAC8 | S | Split System - S | 135000 | 239999 | N/A | N/A | 10.8 | 12.2 | N/A | N/A | N/A | N/A | N/A | 12 | 12 | 14 | 14 | N/A | N/A | 89 | 89 | 15 | 2
HVAC9 | P | Single Package - P | 65000 | 134999 | N/A | N/A | 11 | 12.7 | N/A | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 13 | 13 | N/A | N/A | 73 | 73 | 15 | 1
HVAC10 | P | Single Package - P | 65000 | 134999 | N/A | N/A | 11 | 12.7 | N/A | N/A | N/A | N/A | N/A | 12.5 | 12.5 | 14 | 14 | N/A | N/A | 79 | 79 | 15 | 2
HVAC11 | P | Single Package - P | 135000 | 239999 | N/A | N/A | 10.8 | 12.2 | N/A | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 12.4 | 12.4 | N/A | N/A | 79 | 79 | 15 | 1
HVAC12 | P | Single Package - P | 135000 | 239999 | N/A | N/A | 10.8 | 12.2 | N/A | N/A | N/A | N/A | N/A | 12 | 12 | 14 | 14 | N/A | N/A | 89 | 89 | 15 | 2
HVAC13 | D | Central DX AC - D | 240000 | 759999 | N/A | N/A | 9.8 | 11.4 | N/A | N/A | N/A | N/A | N/A | 10.5 | 10.5 | 11.6 | 11.6 | N/A | N/A | 79 | 79 | 15 | 1
HVAC14 | D | Central DX AC - D | 240000 | 759999 | N/A | N/A | 9.8 | 11.4 | N/A | N/A | N/A | N/A | N/A | 11 | 11 | 12.5 | 12.5 | N/A | N/A | 85 | 85 | 15 | 2
HVAC15 | D | Central DX AC - D | 760000 | 999999999 | N/A | N/A | 9.5 | 11 | N/A | N/A | N/A | N/A | N/A | 9.7 | 9.7 | 11.2 | 11.2 | N/A | N/A | 72 | 72 | 15 | 1
HVAC16 | D | Central DX AC - D | 760000 | 999999999 | N/A | N/A | 9.5 | 11 | N/A | N/A | N/A | N/A | N/A | 10 | 10 | 12 | 12 | N/A | N/A | 77 | 77 | 15 | 2
HVAC17 | AS | Air Source Heat Pump (Split System) - AS | 1 | 64999 | 14 | 8.2 | N/A | N/A | N/A | 14.3 | 14.3 | 8.4 | 8.4 | N/A | N/A | N/A | N/A | N/A | N/A | 92 | 92 | 15 | 1
HVAC18 | AS | Air Source Heat Pump (Split System) - AS | 1 | 64999 | 14 | 8.2 | N/A | N/A | N/A | 15.5 | 15.5 | 8.5 | 8.5 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | 100 | 15 | 2
HVAC19 | AP | Air Source Heat Pump (Single Package) - AP | 1 | 64999 | 14 | 8 | N/A | N/A | N/A | 14.3 | 14.3 | 8.2 | 8.2 | N/A | N/A | N/A | N/A | N/A | N/A | 92 | 92 | 15 | 1
HVAC20 | AP | Air Source Heat Pump (Single Package) - AP | 1 | 64999 | 14 | 8 | N/A | N/A | N/A | 15.5 | 15.5 | 8.5 | 8.5 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | 100 | 15 | 2
HVAC21 | AS | Air Source Heat Pump (Split System) - AS | 65000 | 134999 | N/A | N/A | 10.8 | 11 | 3.3 | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 12.2 | 12.2 | 3.4 | 3.4 | 73 | 73 | 15 | 1
HVAC22 | AS | Air Source Heat Pump (Split System) - AS | 65000 | 134999 | N/A | N/A | 10.8 | 11 | 3.3 | N/A | N/A | N/A | N/A | 12.1 | 12.1 | 12.8 | 12.8 | 3.5 | 3.5 | 77 | 77 | 15 | 2
HVAC23 | AS | Air Source Heat Pump (Split System) - AS | 135000 | 239999 | N/A | N/A | 10.4 | 11.4 | 3.2 | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 11.6 | 11.6 | 3.3 | 3.3 | 79 | 79 | 15 | 1
HVAC24 | AS | Air Source Heat Pump (Split System) - AS | 135000 | 239999 | N/A | N/A | 10.4 | 11.4 | 3.2 | N/A | N/A | N/A | N/A | 11.7 | 11.7 | 15 | 15 | 3.3 | 3.3 | 82 | 82 | 15 | 2
HVAC25 | AS | Air Source Heat Pump (Split System) - AS | 240000 | 999999999 | N/A | N/A | 9.3 | 10.4 | 3.2 | N/A | N/A | N/A | N/A | 9.5 | 9.5 | 10.5 | 10.5 | 3.2 | 3.2 | 78 | 78 | 15 | 1
HVAC26 | AS | Air Source Heat Pump (Split System) - AS | 240000 | 999999999 | N/A | N/A | 9.3 | 10.4 | 3.2 | N/A | N/A | N/A | N/A | 9.7 | 9.7 | 12 | 12 | 3.2 | 3.2 | 82 | 82 | 15 | 2
HVAC27 | AP | Air Source Heat Pump (Single Package) - AP | 65000 | 134999 | N/A | N/A | 10.8 | 11 | 3.3 | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 12.2 | 12.2 | 3.4 | 3.4 | 73 | 73 | 15 | 1
HVAC28 | AP | Air Source Heat Pump (Single Package) - AP | 65000 | 134999 | N/A | N/A | 10.8 | 11 | 3.3 | N/A | N/A | N/A | N/A | 12.1 | 12.1 | 12.8 | 12.8 | 3.5 | 3.5 | 77 | 77 | 15 | 2
HVAC29 | AP | Air Source Heat Pump (Single Package) - AP | 135000 | 239999 | N/A | N/A | 10.4 | 11.4 | 3.2 | N/A | N/A | N/A | N/A | 11.5 | 11.5 | 11.6 | 11.6 | 3.3 | 3.3 | 79 | 79 | 15 | 1
HVAC30 | AP | Air Source Heat Pump (Single Package) - AP | 135000 | 239999 | N/A | N/A | 10.4 | 11.4 | 3.2 | N/A | N/A | N/A | N/A | 11.7 | 11.7 | 15 | 15 | 3.3 | 3.3 | 82 | 82 | 15 | 2
HVAC31 | AP | Air Source Heat Pump (Single Package) - AP | 240000 | 999999999 | N/A | N/A | 9.3 | 10.4 | 3.2 | N/A | N/A | N/A | N/A | 9.5 | 9.5 | 10.5 | 10.5 | 3.2 | 3.2 | 79 | 79 | 15 | 1
HVAC32 | AP | Air Source Heat Pump (Single Package) - AP | 240000 | 999999999 | N/A | N/A | 9.3 | 10.4 | 3.2 | N/A | N/A | N/A | N/A | 9.7 | 9.7 | 12 | 12 | 3.2 | 3.2 | 82 | 82 | 15 | 2
HVAC33 | W | Water Source Heat Pump - W | 1 | 16999 | N/A | N/A | 12.2 | N/A | 4.3 | N/A | N/A | N/A | N/A | 9.7 | 12.4 | N/A | N/A | 4.3 | 4.3 | 40 | 20 | 15 | 1
HVAC34 | W | Water Source Heat Pump - W | 1 | 16999 | N/A | N/A | 12.2 | N/A | 4.3 | N/A | N/A | N/A | N/A | 12.4 | 14 | N/A | N/A | 4.8 | 4.8 | 45 | 23 | 15 | 2
HVAC35 | W | Water Source Heat Pump - W | 17000 | 64999 | N/A | N/A | 13 | N/A | 4.3 | N/A | N/A | N/A | N/A | 14 | 13.3 | N/A | N/A | 4.3 | 4.3 | 60 | 30 | 15 | 1
HVAC36 | W | Water Source Heat Pump - W | 17000 | 64999 | N/A | N/A | 13 | N/A | 4.3 | N/A | N/A | N/A | N/A | 13.3 | 15 | N/A | N/A | 4.5 | 4.5 | 68 | 34 | 15 | 2
HVAC37 | W | Water Source Heat Pump - W | 65000 | 134999 | N/A | N/A | 13 | N/A | 4.3 | N/A | N/A | N/A | N/A | 15 | 13.3 | N/A | N/A | 4.3 | 4.3 | 80 | 40 | 15 | 1
HVAC38 | W | Water Source Heat Pump - W | 65000 | 134999 | N/A | N/A | 13 | N/A | 4.3 | N/A | N/A | N/A | N/A | 13.3 | 15 | N/A | N/A | 4.5 | 4.5 | 90 | 45 | 15 | 2
HVAC39 | PTAC | Packaged Terminal AC - PTAC | 1 | 6999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 12 | 12 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC40 | PTAC | Packaged Terminal AC - PTAC | 7000 | 7999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 12 | 12 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC41 | PTAC | Packaged Terminal AC - PTAC | 8000 | 8999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 11.7 | 11.7 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC42 | PTAC | Packaged Terminal AC - PTAC | 9000 | 9999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 11.4 | 11.4 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC43 | PTAC | Packaged Terminal AC - PTAC | 10000 | 10999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 11.1 | 11.1 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC44 | PTAC | Packaged Terminal AC - PTAC | 11000 | 11999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 10.8 | 10.8 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC45 | PTAC | Packaged Terminal AC - PTAC | 12000 | 12999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 10.5 | 10.5 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC46 | PTAC | Packaged Terminal AC - PTAC | 13000 | 13999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC47 | PTAC | Packaged Terminal AC - PTAC | 14000 | 14999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 9.9 | 9.9 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC48 | PTAC | Packaged Terminal AC - PTAC | 15000 | 999999999 | N/A | N/A | Calc | N/A | N/A | N/A | N/A | N/A | N/A | 9.6 | 9.6 | N/A | N/A | N/A | N/A | 40 | 20 | 15 | 1
HVAC49 | PTHP | Packaged Terminal HP - PTHP | 1 | 6999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 12 | 12 | N/A | N/A | 3.4 | 3.4 | 40 | 20 | 15 | 1
HVAC50 | PTHP | Packaged Terminal HP - PTHP | 7000 | 7999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 12 | 12 | N/A | N/A | 3.4 | 3.4 | 40 | 20 | 15 | 1
HVAC51 | PTHP | Packaged Terminal HP - PTHP | 8000 | 8999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 11.7 | 11.7 | N/A | N/A | 3.3 | 3.3 | 40 | 20 | 15 | 1
HVAC52 | PTHP | Packaged Terminal HP - PTHP | 9000 | 9999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 11.4 | 11.4 | N/A | N/A | 3.3 | 3.3 | 40 | 20 | 15 | 1
HVAC53 | PTHP | Packaged Terminal HP - PTHP | 10000 | 10999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 11.1 | 11.1 | N/A | N/A | 3.2 | 3.2 | 40 | 20 | 15 | 1
HVAC54 | PTHP | Packaged Terminal HP - PTHP | 11000 | 11999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 10.8 | 10.8 | N/A | N/A | 3.2 | 3.2 | 40 | 20 | 15 | 1
HVAC55 | PTHP | Packaged Terminal HP - PTHP | 12000 | 12999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 10.5 | 10.5 | N/A | N/A | 3.1 | 3.1 | 40 | 20 | 15 | 1
HVAC56 | PTHP | Packaged Terminal HP - PTHP | 13000 | 13999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | 3.1 | 3.1 | 40 | 20 | 15 | 1
HVAC57 | PTHP | Packaged Terminal HP - PTHP | 14000 | 14999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 9.9 | 9.9 | N/A | N/A | 3 | 3 | 40 | 20 | 15 | 1
HVAC58 | PTHP | Packaged Terminal HP - PTHP | 15000 | 999999999 | N/A | N/A | Calc | N/A | Calc | N/A | N/A | N/A | N/A | 9.6 | 9.6 | N/A | N/A | 3.1 | 3.1 | 40 | 20 | 15 | 1
HVAC59 | PVAC | Single Packaged Vertical AC - PVAC | 1 | 64999 | N/A | N/A | 10 | N/A | N/A | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | N/A | N/A | 45 | 10 | 15 | 1
HVAC60 | PVAC | Single Packaged Vertical AC - PVAC | 1 | 64999 | N/A | N/A | 10 | N/A | N/A | N/A | N/A | N/A | N/A | 10.7 | 10.7 | N/A | N/A | N/A | N/A | 47 | 12 | 15 | 2
HVAC61 | PVAC | Single Packaged Vertical AC - PVAC | 65000 | 134999 | N/A | N/A | 10 | N/A | N/A | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | N/A | N/A | 45 | 10 | 15 | 1
HVAC62 | PVAC | Single Packaged Vertical AC - PVAC | 65000 | 134999 | N/A | N/A | 10 | N/A | N/A | N/A | N/A | N/A | N/A | 10.7 | 10.7 | N/A | N/A | N/A | N/A | 47 | 12 | 15 | 2
HVAC63 | PVAC | Single Packaged Vertical AC - PVAC | 135000 | 239999 | N/A | N/A | 10 | N/A | N/A | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | N/A | N/A | 45 | 10 | 15 | 1
HVAC64 | PVAC | Single Packaged Vertical AC - PVAC | 135000 | 239999 | N/A | N/A | 10 | N/A | N/A | N/A | N/A | N/A | N/A | 10.7 | 10.7 | N/A | N/A | N/A | N/A | 47 | 12 | 15 | 2
HVAC65 | PVHP | Single Packaged Vertical HP - PVHP | 1 | 64999 | N/A | N/A | 10 | N/A | 3 | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | 3.1 | 3.1 | 45 | 10 | 15 | 1
HVAC66 | PVHP | Single Packaged Vertical HP - PVHP | 1 | 64999 | N/A | N/A | 10 | N/A | 3 | N/A | N/A | N/A | N/A | 10.7 | 10.7 | N/A | N/A | 3.2 | 3.2 | 47 | 12 | 15 | 2
HVAC67 | PVHP | Single Packaged Vertical HP - PVHP | 65000 | 134999 | N/A | N/A | 10 | N/A | 3 | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | 3.1 | 3.1 | 45 | 10 | 15 | 1
HVAC68 | PVHP | Single Packaged Vertical HP - PVHP | 65000 | 134999 | N/A | N/A | 10 | N/A | 3 | N/A | N/A | N/A | N/A | 10.7 | 10.7 | N/A | N/A | 3.2 | 3.2 | 47 | 12 | 15 | 2
HVAC69 | PVHP | Single Packaged Vertical HP - PVHP | 135000 | 239999 | N/A | N/A | 10 | N/A | 3 | N/A | N/A | N/A | N/A | 10.2 | 10.2 | N/A | N/A | 3.1 | 3.1 | 45 | 10 | 15 | 1
HVAC70 | PVHP | Single Packaged Vertical HP - PVHP | 135000 | 239999 | N/A | N/A | 10 | N/A | 3 | N/A | N/A | N/A | N/A | 10.7 | 10.7 | N/A | N/A | 3.2 | 3.2 | 47 | 12 | 15 | 2
HVAC71 | E | A/C Economizing Controls | 1 | 60000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 15 | N/A
HVAC72 | E | A/C Economizing Controls | 60001 | 999999999 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 170 | 170 | 15 | N/A
HVAC73 | O | Occupancy Controlled Thermostats | 0 | 999999999 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 75 | 75 | 11 | N/A

## Table (hidden)
Facility Type | Heating EFLHh | Cooling EFLHc
Assembly | 603 | 669
Auto repair | 1910 | 426
Dormitory | 465 | 800
Hospital | 3366 | 1424
Light industrial | 714 | 549
Lodging – Hotel | 1077 | 2918
Lodging – Motel | 619 | 1233
Office – large | 2034 | 720
Office – small | 431 | 955
Other | 681 | 736
Religious worship | 722 | 279
Restaurant – fast food | 813 | 645
Restaurant – full service | 821 | 574
Retail – big box | 191 | 1279
Retail – Grocery | 191 | 1279
Retail – small | 545 | 882
Retail – large | 2101 | 1068
School – Community college | 1431 | 846
School – postsecondary | 1191 | 1208
School – primary | 840 | 394
School – secondary | 901 | 466
Warehouse | 452 | 400
Multifamily: Low-rise, Prior to 1979 | 757 | 507
Multifamily: Low-rise, From 1979 to 2006 | 723 | 550
Multifamily: Low-rise, From 2007 through present | 503 | 562
Multifamily: High-rise, Prior to 1979 | 526 | 793
Multifamily: High-rise, From 1979 to 2006 | 395 | 843
Multifamily: High-rise, From 2007 through present | 219 | 954

## Export (hidden)
Measure Type | Manufacturer | Model | Capacity/Size | Capacity/Size Units | EER Efficiency | SEER Efficiency | Incentive Per Unit | Quantity Committed | Annual Electricity Savings | Peak Demand Reduction | Lifetime Electricity Savings | Annual Gas Savings | Lifetime Gas Savings | Efficiency- other | Efficiency- other-type | Measure ID removed | Quantity Installed | Project in UEZ | Project in OZ | Municipality | K-12 School | County | Affordable Housing | Enhanced Incentive per Unit
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0
|  |  | 0 | Btuh |  | 0 | 0 |  | 0 | 0 | [7 empty] | N | N | N | N | N | N | 0

## Version (hidden)
13 | <-Version
Log
1/1/2008 Baseline efficiencies updated to comply with new protocol
12/1/2008 updated for measure tracking compatability
7/13/2009 entered formula for baseline efficiency into "n"-column cells to reflect protocol.
10/18/2009 added separate Dual Enthalpy Control system in order for correct incentive to export
(missed updates)
2011-03-15 |  | fixed error in export tab where the quantity was left out in a certain row
2012-01-13 | V5 | added fuel use economizers
2013-07-09 | V7 | no change for V7, skipped V6
2014-08-13 |  | updated dual enthalpy formula for demand savings in VBA code; updated central dx baseline to match other DX systems, also in VBA code
2018-06-21 | V12 | Removed Dual Enthalpy Economizer measure and updated to align with FY19 Protocols
2019-07-01 | V13 | Added Enhanced Incentive Eligibility Section and Updated for FY20 Program