## Elevator Calculator
Pay for Performance - NC
Technical Tip: Calculating Elevator Energy Consumption
Instructions: Please fill out the blue cells with the Design and Baseline elevator parameters. The white cells showing results in rows 45-51 will auto populate based on the blue cells.
| Elevator ID | 1 | 2 | 3 | 4 | 5
Application | Elevator Name | Car 1 | Car 2
| Quantity | 4 | 1
| Passanger or service elevator? | Passenger | Service
| Buildings and elevator type | Office or administrative building 6 - 10 floors | Goods lift with few operations
| Average Travel Time (hours per day) | 1.5 | 0.5 | 0 | 0 | 0
| Usage Type: Intensity/ Frequency | Medium/ Occasionally | Low/ Seldom | - | - | -
| Number of Stories Served (including below grade floors) | 10 | 10
Proposed Design | Counterweight of Car (lbs) (if unknown, leave blank)
| Weight of Car (lb.) | 8098 | 8824
| Rated Load (lb.) | 3500 | 4000
| Speed of Car (ft./min) | 1200 | 1200
| bhp | 81.94 | 53.43
| Motor efficiency (%) | 94.5% | 93.6%
| Cabin Fan Power (Watt) | 90 | 90
| Cabin Airflow (CFM) | 325 | 325
| Cabin Lighting Power (Watt) | 100 | 100
| Cabin Occupancy Sensor Lighting Controls (Y/N) | Yes | Yes
| Cab Area (Square Feet) | 56 | 56
Proposed kWh | Peak Motor Power per Motor, Pm (kW) | 64.7 | 42.6
| Annual Motor Energy Use (kWh/yr) | 141693 | 7774.5
| Annual Cabin Fan Energy Use (kWh/Yr) | 3153.6 | 788.4 | 0 | 0 | 0
| Annual Cabin Lighting Energy Use (kWh/Yr) | 219 | 18.3 | 0 | 0 | 0
Baseline kWh | Baseline Parameters
| Cab Lighting Power Allowance (W/SF) | 3.14 | 3.14 | - | - | -
| Cab Fan Power Allowance (W/CFM) | 0.33 | 0.33 | - | - | -
| Baseline Elevator Type | Traction | Traction | - | - | -
| Counterweight [weight of car + 40% of rated load] (lb.) | 9498 | 10424 | 0 | 0 | 0
| Cab Mechanical Efficiency [h mechanical] (%) ASHRAE 90.1-2016 Table G3.9.2 | 64% | 64% | - | - | -
| bhp | 119.3 | 136.4
| Traction Motor Efficiency | 94.5% | 95%
| Hydraulic Motor Efficiency | 80% | 80%
| Cab Motor Efficiency [h motor] (%) ASHRAE 90.1-2016 Tables G3.9.3 & G3.9.1 | 94.5% | 95%
| Peak Motor Power per Motor, Pm (kW) | 94.2 | 107.1
| Annual Motor kWh/yr | 206298 | 19545.8
| Annual Fan kWh/Yr | 3758 | 939.5
| Annual Light kWh/Yr | 6161.4 | 1540.4
Savings Summary
| Building | Annual Electric Consumption (kWh)
|  | Baseline | Proposed | Savings
| Motor | 225843.8 | 149467.5 | 76376.3
| Fans | 4697.5 | 3942 | 755.5
| Lights | 7701.8 | 237.3 | 7464.5
| Total | 238243.1 | 153646.8 | 84596.3

## Table 1 Usage Categories (hidden)
Table 1
Usage Category | 1 | 2 | 3 | 4 | 5
Usage Intensity/ Frequency | Very Low Very Seldom | Low Seldom | Medium Occasionally | High Frequently | Very High Very Frequently
Average Travel Time (hours per day) | 0.2 | 0.5 | 1.5 | 3 | 6
Typical Type of Buildings and Use | Residential building with up to 6 dwellings. Small office or administrative building with few operations. | Residential building with up to 20 dwellings. Small Office or Administrative Building with 2 to 5 floors. Small Hotels Goods lift with few operations. | Residential building with up to 50 dwellings. Small office or administrative building with up to 10 floors. Medium Sized Hotels Goods lift with medium operations. | Residential building with more than 50 dwellings. Tall office or administrative building with more than 10 floors. Large Hotel Small to Medium Sized Hospitals Good lift in production process with a single shaft. | Office or administration building over 100 meters in height. Large Hospital Goods lift in production process with several shafts.

## Motor Efficiency (hidden)
Table G3.9.3 Motor Efficiency Requirements for Hydraulic Motors
Horsepower | Full-Load Efficiency
10 | 72%
20 | 75%
30 | 78%
40 | 78%
100 | 80%
Table G3.9.1 Motor Efficiency Requirements for Traction Motors
Horsepower | Full-Load Efficiency
1 | 82.5%
1.5 | 84%
2 | 84%
3 | 87.5%
5 | 87.5%
7.5 | 89.5%
10 | 89.5%
15 | 91%
20 | 91%
25 | 92.4%
30 | 92.4%
40 | 93%
50 | 93%
60 | 93.6%
75 | 94.1%
100 | 94.5%
125 | 94.5%
150 | 95%
200 | 95%

## Usage hours (hidden)
Typical Type of Building | Use (hours/day)
Residential building with up to 6 dwellings | 0.2 | 0.2 | Very Low/ Very Seldom
Residential building with 7 - 20 dwellings | 0.5 | 0.5 | Low/ Seldom
Residential building with 21 – 49 dwellings. | 1.5 | 1.5 | Medium/ Occasionally
Residential building with more than 50 dwellings | 3 | 3 | High/ Frequently
Office or administrative building, small with few operations | 0.2 | 6 | Very High/ Very Frequently
Office or administrative building 2 - 5 floors | 0.5
Office or administrative building 6 - 10 floors | 1.5
Office or administrative building with more than 10 floors | 3
Office or administration building over 300 feet in height | 6
Hotel, small | 0.5
Hotel, medium | 1.5
Hotel, large | 3
Hospital, small to medium | 3
Hospital, large | 6
Goods lift with few operations | 0.5
Goods lift with medium operations. | 1.5
Goods lift in production process with a single shaft | 3